Amensolar N3H-X XX.0-US Hybrid Inverter Setup Procedure

Verify that the firmware version of the inverter is at the the following levels:

Arm: 3.06
Dsp: 4.06

If not, download the zipped setup file from the test server and place both the hybrid_appLNAV23_20230613.axf and the HybridInverter8KSNA_v1.4.13_B03D27_20230605 files on the desktop. Connect a USB type C cable from your computer to the inverters USB connector located to the left hand side of the top row of RJ6 modular receptacles.

First import the hybrid_appLNAV23_20230613.axf file and then select upgrade. Next import the
HybridInverter8KSNA_v1.4.13_B03D27_20230605 file and select upgrade.

1. Log into the Setup Setting (item 1) with the password: 00000
2. Set the Work Mode value to bat priority.
3. Set the EPS enable value to enabled.
4. Set the Bat Wake Up value to disabled.
5. Set the PV input value to the configuration of the PV array (usually independent).
6. Set the Grid Sell value to no.
7. Set the Home Load value to disabled.
8. Set the ARC Enable value to disabled.
9. Set the RSD Switch value to enabled.
10. Select the Bat setting (item 2) and select Lithium as the battery type.
11. Under the Disc-depth setting set both the grid DOD and the off grid DOD values to 80 %, then set the return value to 20 %.
12. The Charge current represents the maximum current the inverter will charge the inverters battery at, this value is dependent on the size of generator (when generator connected) or the size of the breakers when using an attached SSR 'grid to generator port' interface. A good value to use is 40 Amps.
13. Under the Batt Comm setting select CAN as the communications type.
14. Under the Generator setting (item 15) set the Start SOC value to the desired level in which you want the generator to start at. A typical value is usually 50 to 60 percent. Note: This value must be 1% higher than that set on the AGS SOC.
15. Set the stop SOC value to 100%
16. Set the charge current to battery to the same value as setup to in item 4 above.
17. Set the maximum run time to 8 hours.
18. Under the generator control setting, set generator en setting to enabled.
19. Under the gen-chg-en (generator charge enable) select enabled.
20. Under the manual-en (manual enable) select disabled.
21. Under the manual-Cmd-en (manual command enable) select disabled.
22. Under the connect to grid setting select disabled.
23. Under the power setting enter the value of the inverters rating 10 KW, 8 KW, or 12 KW
24. Under the Advanced settings (item 16) set the mode set the value to disabled.
25. Under the Advanced control setting set the grid Chg En set the value to disabled.
26. Under the TOU En setting set the value to disabled.
27. Under the OnlyPVchg setting set the value to disabled.